## QA BESS RFP
# | Question | Answer
1 | Why can’t we design the substation at Balls Ford to be at 34.5kV instead of the current design of 13.2kV? | The new utility substation will be designed to include additional distribution circuits that are typically 15kV. The termination points will need to respect that design.
2 | Are Section H and Attachment 3, section 1.3 required for Phase 1 submission? | No; Those sections are related to the Offer presentation.
3 | Confirm all substation scopes fall under NOVEC SOW and NOVEC will provide the MV connection(s) to the BESS sites? | That is correct.
4 | Confirm that Perimeter site will follow NEC grounding requirements and will not be held to IEEE80 standards? | The grounding equipment for the entire Balls Ford site will be installed by NOVEC as part of the substation installation. The BESS EPC will need to connect their equipment to that grounding mat. The Perimeter site will need to meet the IEEE requirements.
5 | Will NOVEC handle the site plan submissions for both BESS sites with the county? | NOVEC is currently using a proxy site layout for the county approval process. NOVEC will address noise abatement and fire requirements for the sites in the county approval process.
6 | Will AHJ permitting be required for building permits? | As part of the county approval process, if there are any AHJ requirements that differ from industry standard requirements, NOVEC will pass those requirements along once NOVEC becomes aware of any.
7 | Since the Perimeter BESS site is only a single feed to the BESS station and has a 50MW capacity, would parallel feeders in that single run be acceptable as we would need that for a single POI at the BESS site? | Yes; That should be acceptable.
8 | Does NOVEC intend to augment the system in future? If so, does space need to be developed and readied for the future expansion? | Not at this point in time.
9 | Please confirm that EPC contractor will be providing BESS, PCS, EMS equipment for both sites. It seems to be implied, but not explicitly stated in the RFP? | Yes.
10 | Please confirm Perimeter BESS site AC POI power requirement is 50MW? | 50MWac at the POI.
11 | Please confirm the capacity required at the POI for PERI. E.g., is it 50MW at the POI or is it 50MW nameplate of the system, which would yield a lower capacity at POI? | 50MWac at the POI.
12 | Are microgrid and blackstart capabilities required? | No.
13 | Would NOVEC consider a tolling arrangement at the two locations in lieu of a built own transfer? | No; NOVEC already has some BESS projects that are tolling arrangements. These two projects are to be owned and operated by NOVEC.
14 | Would NOVEC be interested in other or more locations on their system for a BESS? | NOVEC is exploring additional locations for future projects within its service territory.
15 | Would the BESS resource developed under this procurement be considered a Non Retail Behind the Meter Generator by PJM? | NOVEC could register these facilities as NrBTMG with PJM if there are benefits to do so.
16 | What are the storm water runoff requirements at both sites? | Will be confirmed with the county permit process.
17 | What are the fire requirements at both sites? | Will be confirmed with the county permit process.
18 | What Geotech information do you have for both sites that can be shared with bidders? | The Perimeter site had 10 borings and that report will be provided. NOVEC will include in its SOW the installation of the concrete pads for the BESS batteries. The Balls Ford site also has concrete pads under the visible gravel and the site drawing of those pads will be provided.
19 | What are the noise restrictions and requirements at both sites? | Will be confirmed with the county permit process.